- Part 1 – General

  - SECTION INCLUDES

- Labor, products, equipment, and services necessary for a Quartz Flooring System in accordance with the Contract Drawing & Schedules covering the following components:

- Primer: Ecocrete Coatings Moisture Barrier Primer

- Cove (if applicable): Ecocrete Coatings Epoxy Clear with Epoxy Thickener & Color Quartz Blend

- Double Broadcast Coats & Grout Coat: Ecocrete Coatings Epoxy Clear

- Aggregate: Ecocrete Coatings Color Quartz Blend

- Top Coat: Ecocrete Coatings Urethane-CR Clear Gloss

  - RELATED SECTIONS

- A.	Section 03 30 00 – Cast-in-Place Concrete

- B. 	Section 03 39 00 – Concrete Curing

  - REFERENCES

- ASTM D695, Standard Test Method for Compressive Strength

- ASTM D638, Standard Test Method for Tensile Properties of Plastics

- ASTM D4541, Standard Test Method for Bond Strength to Concrete

- ASTM D790, Standard Test Method for Flexural Strength

- ASTM D3363, Standard Test Method for Hardness

- For additional standards, please refer to Product Data Sheets.

  - SUBMITTALS

- Comply with Section 01 33 00 – Submittal Procedures.

- Product Data: Submit manufacturer’s product data, including physical properties and colors available.

- Safety Data Sheet for each product being used.

- Product Samples: Submit Architectural Standard samples representative of the final finish, as applied. The Standard shall be approved in writing by the Architect and shall be the final standard of acceptance of the finish.

- Maintenance Instructions: Submit manufacturer’s maintenance instructions.

  - QUALITY ASSURANCE

- Manufacturer Qualifications

  - Acceptable Manufacturer: Ecocrete Coatings, Inc., 258 E 10th Drive, Mesa, Arizona, 85211

  - No requests for substitutions shall be considered that would change the generic type of the specified System

  - System shall be in compliance with requirements of United States Department of Agriculture (USDA), Food Drug Administration (FDA), and local Health Department.

- Applicator Qualifications

  - The Applicator shall have been approved by the flooring system manufacturer in all phases of surface preparation and application of the product specified.

- Acceptance of Sample/Mock-up

  - Arrange for Architect/Engineer’s review and acceptance, obtain written acceptance before proceeding with Work.

- Pre-application Meeting

  - Arrange a pre-application meeting two (2) weeks before start of application of floor coating. Require attendance of parties directly affecting work of this section, including Owner, Architect, General Contractor, Applicator and manufacturer’s representative to review surface preparation, application procedure, curing, protection, and coordination with other work.

  - DELIVERY, STORAGE, HANDLING, DISPOSAL

- Delivery

- All components of the system shall be delivered to the site in the Manufacturer's original, unopened containers and packaging, with labels clearly identifying product manufacturer, name, date, and batch number.

- Material should be delivered to job site and checked for correctness and shipping damage prior to job start.

- Storage

- Store materials in accordance with manufacturer’s written instructions.

- The Applicator shall be provided with a storage area for all components. The area shall be between 60˚F and 90˚F, dry, enclosed, protected area from the elements.

- Do not subject material to excessing heat or freezing.

- Copies of Safety Data Sheets (SDS) for all components shall be kept on site for review by the Engineer or other personnel.

- Handling

- Protect materials during handling and application to prevent damage or contamination.

- Condition materials for use accordingly to manufacturer’s written instructions prior to application.

- Record material lot number and quantity delivered to jobsite/storage.

- Waste Disposal

  - The Applicator shall be provided with adequate disposal facilities for non-hazardous waste generated during installation of the system.

  - PROJECT CONDITIONS

- Application Temperatures

SPECIFIER’S NOTE:

Do not install the Work of this Section if temperatures are outside listed range without the Manufacturer’s written acceptance.

- Application may proceed while air, material and substrate temperatures are between 50˚F and 100˚F providing the substrate temperature is 5˚F above the dew point.

- The relative humidity in the specific location of the application shall be less than 85% and the surface temperature shall be at least 5˚F above the dew point.

- Mixing and Application attempted at Material, Ambient and/or Substrate Temperature conditions less than 65˚F (18˚C) will result in a decrease in product workability and slower cure rates.

- Site Requirements

- Insure adequate ventilation and air flow is available for the work area.

- Utilities, including electric, water, HVAC, and permanent lighting during the preparation and installation of the system to be supplied by the General Contractor.

- Erect suitable barriers and post legible signs at points of entry to prevent traffic and trades from entering the work area during application and cure period of the floor.

- Protection of finished floor from damaged by subsequent trades shall be the responsibility of the General Contractor.

- Conditions of new concrete to be coated with epoxy material.

- Concrete shall be moisture cured for a minimum of 7 days and have fully cured a minimum of twenty-eight days in accordance with ACI-308 prior to the application of the coating system pending moisture tests.

- Concrete shall have a flat rubbed finish, float, or light steel trowel finish (a hard steel trowel finish is neither necessary or desirable).

- Sealers and curing agents should not to be used.

- Concrete surfaces on grade shall have been constructed with a vapor barrier to protect against the effects of vapor transmission and possible delamination of the system.

- Safety Requirements

- All open flames and spark-producing equipment shall be removed from the work area prior to commencement of application.

- "No Smoking" signs shall be posted at the entrances to the work area.

- Food Industry Environment: The Owner shall be responsible for the removal of food from the work area.

- Non-related personnel in the work area shall be kept to a minimum.

  - WARRANTY

- Ecocrete Coatings, Inc. warrants that material shipped to buyers at the time of shipment is substantially free from material defects and will perform substantially to Ecocrete Coatings, Inc. published literature if used in accordance with the latest prescribed procedures and prior to the expiration date.

- Ecocrete Coatings, Inc. liability with respect to this warranty is strictly limited to the value of the material purchase.

- Part 2 – Products

  - MANUFACTURER

- Approved Manufacturer shall be Ecocrete Coatings, Inc., 258 East 10th Dr, Mesa, Arizona 85210, Phone 480.361.6887, Fax 480.644.8252, www.ecocretecoatings.com

2.2	SYSTEM

Ecocrete Coatings’ Eco-Quartz Floor is an 1/8” thick, seamless, chemical resistant floor system. Eco-Quartz Floor is a fluid applied epoxy floor system comprised of a moisture remediation epoxy primer, 100% solids clear epoxy with a double broadcast of a decorative color quartz blend, a grout coat of 100% solids clear epoxy and a chemical resistant, aliphatic, clear urethane top coat.

      - Resinous flooring system: Eco-Quartz Floor flooring system consist of the following components:

            - Primer:  Ecocrete Coatings Moisture Barrier Primer.

            - Cove (if applicable): Ecocrete Coatings Epoxy Clear with Epoxy Thickener & Color Quartz Blend

            - Double Broadcast Coats & Grout Coat: Ecocrete Coatings Epoxy Clear

            - Aggregate: Ecocrete Coatings Color Quartz Blend

            - Top Coat:  Ecocrete Coatings Urethane-CR Clear Gloss

      - Patch Materials

  - Shallow Fill and Patching:  Use Ecocrete Coatings Epoxy Clear with Epoxy Thickener

  - Cove Base, Deep Fill and Sloping (over ¼”): Use Ecocrete Coatings Epoxy Clear with Epoxy Thickener and Color Quartz Blend

  - MATERIALS

      - Moisture Barrier Primer is a two component, high performance moisture remediation epoxy primer with the following properties:

- Solids by Weight					100%

- VOC								0 g/L

- Adhesion to Concrete, ASTM D4541			450-600 psi

- Compressive Strength, ASTM D695			8,000 psi

- Shore Hardness						85

- Tensile Strength, ASTM C307				8,000 psi

- Water Absorption, Gain in 24hrs, ASTM D570		<1%

      - Epoxy Clear is a two component, 100% solids epoxy coating system in clear with the following properties:

- Solids by Weight					100%

- VOC								0 g/L

- Adhesion to Concrete, ASTM D4541			450 psi

- Compressive Strength, ASTM C579			11,200 psi

- Tensile Strength, ASTM C307				7,000 psi

- Water Absorption, Gain in 24hrs, ASTM D570		<1%

      - Urethane-CR Gloss is a two component, high solids, aliphatic protective coating system in clear with the following properties:

- Solids by Weight					63%

- VOC								449 g/L

- Flexibility ASTM D222 1/8” mandrel    			Passes

- Abrasion Resistance, ASTM D 4060

CS 17 wheel (1 Kg load) 1,000 cycles		35 mg loss

- Pot Life 75˚F						25 minutes

- Working Time 75˚F					30 minutes

- Cure Time						12 hours

- Chemical Resistance					5-7 days

Part 3 – Execution

  - EXAMINATION

      - Applicator to examine substrate areas and conditions to receive flooring system for compliance with requirements for maximum moisture content, installation tolerances and other conditions affecting flooring performance. Notify Architect, General Contractor, Owner, and/or owner’s representative if areas are not acceptable. Do not begin surface preparation or application until unacceptable conditions have been corrected. Do not apply substrate treatments for moisture, repair, or leveling not of the same Manufacturer or approved by Manufacturer.

      - Surface must be clean, sound, and dry. Remove dust, laitance, grease, curing compounds bond inhibiting impregnations, waxes, and any other contaminants. All projections, rough spots, etc. should be removed to achieve a level surface prior to the application.

      - Substrate Moisture:

- Measure and confirm Substrate Moisture Content, Ambient Relative Humidity, Ambient and Surface Temperature and Dew Point.

- Confirm and recover above values at least once every 3 hours during installation or more frequently whenever conditions change (e.g. Ambient Temperature rise/fall, Relative Humidity increase/decrease, etc.)

- Ensure concrete substrate conforms to the minimum requirements of the flooring manufacturer.

  - SURFACE PREPARATION

      - Prepare surface to receive flooring system in accordance with manufacturer’s written instructions.

      - Remove, dirt, oil, grease, wax, laitance, curing compounds, water-soluble concrete hardeners, and other surface contaminants. Remove sealers, finishes, and paints. Remove unsounds concrete by appropriate mechanical means.

      - Moisture Testing:  Perform tests recommended by manufacturer and as follows.

- Perform anhydrous calcium chloride test ASTM F1869. Application will proceed only when the vapor/moisture emission rates from the slab is less than and not higher than 10 lbs/1,000 ft2/24 hrs.

- Perform relative humidity test using in situ probes, ASTM F2170.  Proceed with installation only after substrates have a maximum 98% relative humidity level measurement.

- If the vapor emission exceeds 98% relative humidity and/or 10 lbs/1,000 ft2/24 hrs, then a second coat of Ecocrete Coatings Moisture Barrier Primer at 10 mils must be used as a mitigation system for up to 20 lbs/1,000 ft2/24 hrs – it must be installed prior to resinous flooring installation.  Slab-on grade substrates without a vapor barrier may also require the moisture mitigation system.

      - There shall be no visible moisture present on the surface at the time of application of the system. Compressed oil-free air and/or a light passing of a propane torch may be used to dry the substrate.

      - Mechanical surface preparation:

            - Diamond grind and/or Shot blast all surfaces to receive flooring system with a dust recycling machine (Blastrac or equal).  All surface and embedded accumulations of paint, toppings, hardened concrete layers, laitance, power trowel finishes and other similar surface characteristics shall be completely removed, leaving a bare concrete surface having a minimum profile of CSP 2-3 as described by the International Concrete Repair Institute.

  - Floor areas inaccessible to the mobile prep machines shall be mechanically abraded to the same degree of cleanliness, soundness and profile using diamond grinders, needle guns, bush hammers, or other suitable equipment.

- Where the perimeter of the substrate to be coated is not adjacent to a wall or curb, a minimum ¼ inch key cut shall be made to properly seat the system, providing a smooth transition between areas.  The detail cut shall also apply to drain perimeters and expansion joint edges.

- Cracks and joints (non-moving) greater than ⅛ inch wide are to be opened using a diamond crack chaser and repaired per manufacturer’s recommendations.

- At spalled or worn areas, mechanically remove loose or delaminated concrete to a sound concrete and patch per manufactures recommendations.

  - APPLICATION

- Immediately prior to the application of any component of the system, the surface shall be dry and any remaining dust or loose particles shall be removed using a vacuum or clean, dry, oil-free compressed air.

- The handling, mixing and addition of components shall be performed in a safe manner to achieve the desired results in accordance with the Manufacturer's recommendations.

- The system shall follow the contour of the substrate unless pitching or other leveling work has been specified by the Architect.

- A neat finish with well-defined boundaries and straight edges shall be provided by the Applicator.

- 1st Step – Primer:

- The primer shall consist of two components as supplied by the Manufacturer and mixed at the ratio of 3 parts A : 2 parts B.

- The primer shall be applied by a notched squeegee and back rolled at the rate of 160 ft2/gal.

- Allow to cure.

SPECIFIER’S NOTE:

All repairs and patching are to be completed after application of primer.

- 2nd Step – Cove (if applicable):

- The cove shall consist of Epoxy Clear with Epoxy Thickener & Color Quartz Blend.

- The cove shall be applied as per detailed instructions on Epoxy Thickener’s technical data sheet.

- 3rd Step – 1st Broadcast Coat

- The broadcast coat shall consist of two components as supplied by the Manufacturer and mixed at the ratio of 3 parts A : 2 parts B.

- Both components shall be mixed thoroughly.

- The broadcast coat shall be applied over horizontal surfaces using a notched squeegee and back rolled at the rate of 100 ft2/gal.

- Aggregate shall be broadcasted to rejection into the wet material at the rate of 50 lbs/80-100 ft2.

- Allow material to fully cure. Vacuum, sweep and/or blow to remove all loose aggregate. Then scrape floor and vacuum again.

- 4th Step – 2nd Broadcast Coat

- The broadcast coat shall consist of two components as supplied by the Manufacturer and mixed at the ratio of 3 parts A : 2 parts B.

- Both components shall be mixed thoroughly.

- The broadcast coat shall be applied over horizontal surfaces using a squeegee and back rolled at the rate of 80 ft2/gal.

- Aggregate shall be broadcasted to rejection into the wet material at the rate of 50 lbs/80-100 ft2.

- Allow material to fully cure. Vacuum, sweep and/or blow to remove all loose aggregate. Then scrape floor and vacuum again.

- 5th Step – Grout Coat

- The grout coat shall consist of two components as supplied by the Manufacturer and mixed at the ratio of 3 parts A : 2 parts B.

- The grout coat shall be squeegee applied and back rolled with a coverage rate of 80 ft2/gal.

- Allow to cure.

- 6th Step – Top Coat

- The top coat shall consist of two components as supplied by the Manufacturer and mixed at the ratio of 2 parts A : 1 part B.

- The top coat shall be squeegee applied and back rolled with a coverage rate of 320 ft2/gal.

- Allow to cure.

- The finish floor will have a nominal thickness of 1/8”.

  - CLEAN UP

      - Remove masking.  Perform detail cleaning at floor termination, to leave cleanable surface for subsequent work of other sections.

      - Disposal of this product, solution, and any by-products in accordance with local, state, and federal regulations.

  - FIELD QUALITY CONTROL

A.	The following tests shall be conducted by the Applicator:

  - Temperature: Air, substrate temperatures and, if applicable, dew point.

  - Coverage Rates: Rates for all layers shall be monitored by checking quantity of material used against the area covered.

  - PROTECTION

SPECIFIER’S NOTE:

Under certain conditions, cure times, recoat times, and return to service time may be shortened or lengthened due to environmental conditions. Consult Manufacturer’s Product Data Sheets and review job site conditions to determine if shorter times can be achieved.

      - Cure flooring material in compliance with manufacturer’s directions, taking care to prevent their contamination during stages of application and prior to completion of the curing process.

      - Beware of air flow and changes in air flow. Introduction of dust, debris, and particles, etc. may result in surface imperfections and other defects.

      - Follow manufacturer’s written recommendation with respect to cure, wait time, and return to service.

END OF SECTION

All information provided by Ecocrete Coatings, Inc. (“Ecocrete”) concerning Ecocrete products, including but not limited to, any recommendations and advise relating to the application and use of Ecocrete products, is give in good faith base on Ecocrete’s current experience and knowledge of its products when properly stored, handled, and applied under normal conditions in accordance with Ecocrete’s instructions. In practice, the differences in materials, substrates, storage and handling conditions, actual site conditions and other factors outside of Ecocrete’s control are such that Ecocrete assumes no liability for the provision of such information, advise, recommendations or instructions related to its products, nor shall any legal relationship be created by or arise from the provision of such information, advise, recommendations or instructions related to its products, the user of Ecocrete product(s) must test the product(s) for suitability for the intended application and purpose before proceeding with the full application of the product(s).

Ecocrete reserves the right to change the properties of its products without notice. All sales of Ecocrete product(s) are subject to its current terms and conditions of sale that are available at www.ecocretecoatings.com or by call 480.361.6887.

Prior to each use of any Ecocrete product, the user must always read and follow the warning and instructions on the product’s most current Technical Data Sheet, product label and Safety Data Sheet that are available at www.ecocretecoatings.com or 480.361.6887. Nothing contained in any Ecocrete materials relieves the user of the obligation to read and follow the warnings and instructions for each Ecocrete product as set forth in the current Technical Data Sheet, product label and Safety Data Sheet prior to product use.